- 4.13  Command summary

Table 4-4 lists the functions and data structures for universal commands in HART Revision 5.  Table 4-5 shows the differences in universal commands in earlier revisions of HART.  (Host devices should implement these if they need to operate with older field devices.)  Table 4-6 lists common-practice commands in HART Revision 5, and includes notes (n.n) of the revision in which certain features were introduced.

Notes:	In these tables, data types are indicated as follows:

A	ASCII string (packed 4 characters per 3 bytes)

B	Bit-mapped flags

D	Date (3 bytes: day, month, year-1900)

F	Floating point (4 bytes IEEE 754)

H	Integers xxxxx yyy (xxxxx = hardware revision, yyy = physical signalling code)

- Unmarked items are 8-, 16- or 24-bit integers (including enumerated code values).

- Table 4-4.  Universal commands in HART Revision 5

| Command number and function |  |  | Data in command |  |  | (type) | Data in reply |  |  | (type) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | Read unique identifier |  | none |  | Byte 0 Byte 1 Byte 2 Byte 3 Byte 4 Byte 5 Byte 6 Byte 7 Byte 8 Byte 9-11 Byte 12 ** Byte 13 ** Byte 14 ** Byte 15 ** | "254" (expansion) manufacturer identification code manufacturer's device type code number of preambles required universal command revision device-specific command revision software revision hardware revision device function flags* device ID number common-practice command revision common tables revision data link revision device family code | (H) (B) |
|  |  |  |  |  | * Bit 0 = multisensor device; bit 1 = EEPROM control required; bit 2 = protocol bridge device. ** Proposed for a future HART revision  not in 5.3. |  |  |  |  |
| 1 | Read primary variable |  | none |  | Byte 0 Byte 1-4 | PV units code primary variable | (F) |
| 2 | Read current and percent of range |  | none |  | Byte 0-3 Byte 4-7 | current (mA) percent of range | (F) (F) |
| 3 | Read current and four (predefined) dynamic variables |  | none |  | Byte 0-3 Byte 4 Byte 5-8 Byte 9 Byte 10-13 Byte 14 Byte 15-18 Byte 19 Byte 20-23 | current (mA) PV units code primary variable SV units code secondary variable TV units code third variable FV units code fourth variable | (F) (F) (F) (F) (F) |
|  |  |  |  |  | (truncated after last supported variable) |  |  |  |  |
| 6 | Write polling address | Byte 0 | polling address |  |  | as in command |  |
| 11 | Read unique identifier associated with tag | Byte 0-5 | tag | (A) | Byte 0-11 | as Command #0 |  |
| 12 | Read message |  | none |  | Byte 0-23 | message (32 characters) | (A) |
| 13 | Read tag, descriptor, date |  | none |  | Byte 0-5 Byte 6-17 Byte 18-20 | tag (8 characters) descriptor (16 characters) date | (A) (A) (D) |

| 14 | Read PV sensor information |  | none |  | Byte 0-2 Byte 3 Byte 4-7 Byte 8-11 Byte 12-15 | sensor serial number units code for sensor limits & min. span upper sensor limit lower sensor limit minimum span | (F) (F) (F) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | Read output information |  | none |  | Byte 0 Byte 1 Byte 2 Byte 3-6 Byte 7-10 Byte 11-14 Byte 15 Byte 16 | alarm select code transfer function code PV/range units code upper range value lower range value damping value (seconds) write-protect code private-label distributor code | (F) (F) (F) |
| 16 | Read final assembly number |  | none |  | Byte 0-2 | final assembly number |  |
| 17 | Write message | Byte 0-23 | message (32 chars) | (A) |  | as in command |  |
| 18 | Write tag, descriptor, date | Byte 0-5 Byte 6-17 Byte 18-20 | tag (8 characters) descriptor (16 chars) date | (A) (A) (D) |  | as in command |  |
| 19 | Write final assembly number | Byte 0-2 | final assembly number |  |  | as in command |  |

Table 4-5.  Universal commands in HART Revisions 2, 3 and 4 (differences from Revision 5)

| Command number and function |  |  | Data in command |  |  | (type) | Data in reply |  |  | (type) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | Read unique identifier |  | none |  | Byte 0 Byte 1 Byte 2 Byte 3 Byte 4 Byte 5 Byte 6 Byte 7-9 | transmitter type code * number of preambles universal command revision device-specific command revision software revision hardware revision device function flags final assembly number | (H) (B) |
|  |  |  |  |  | * Revision 4 introduced the expanded device type as an option (see Rev. 5, Table 4-4), with the remaining bytes moved up by two positions. |  |  |  |  |
| 4 | Read common static data (block 0): Read message | Byte 0 | block number ("0") |  | Byte 0 Byte 1-24 | block number ("0") message | (A) |
| 4 | Read common static data (block 1): Read tag, descriptor, date | Byte 0 | block number ("1") |  | Byte 0 Byte 1-6 Byte 7-18 Byte 19-21 Byte 22-24 | block number ("1") tag descriptor date "250" | (A) (A) (D) |
| 4 | Read common static data (block 2): Read sensor information | Byte 0 | block number ("2") |  | Byte 0 Byte 1-3 Byte 4 Byte 5-8 Byte 9-12 Byte 13-16 Byte 17-24 | block number ("2") sensor serial number units code for sensor limits & min. span upper sensor limit lower sensor limit minimum span "250" | (F) (F) (F) |
| 4 | Read common static data (block 3): Read output information | Byte 0 | block number ("3") |  | Byte 0 Byte 1 Byte 2 Byte 3 Byte 4-7 Byte 8-11 Byte 12-15 Byte 16 Byte 17 Byte 18-24 | block number ("3") alarm select code transfer function code PV/range units code upper range value lower range value damping value (seconds) write-protect code ("1" = protected) * private-label distributor code ** "250" | (F) (F) (F) |
|  |  |  |  |  | * "250"or "251" in Revisions 2 and 3. ** "250" in Revisions 2 and 3. |  |  |  |  |
| 5 | Write common static data (block 0): Write message | Byte 0 Byte 1-24 | block number ("0") message | (A) |  | as in command |  |
| 5 | Write common static data (block 1): Write tag, descriptor, date | Byte 0 Byte 1-6 Byte 7-18 Byte 19-21 Byte 22-24 | block number ("1") tag descriptor date "250" | (A) (A) (D) |  | as in command |  |
| 5 | Write common static data (block 4): Write final assembly number | Byte 0 Byte 1-3 Byte 4-24 | block number ("4") final assembly number "250" |  |  | as in command |  |
| 11 - 19 |  |  | These commands did not exist before Revision 5.0 |  |  |  |  |  |  |  |  |  |  |

Table 4-6.  Common-practice commands

| Command number and function |  |  | Data in command |  |  | (type) | Data in reply |  |  | (type) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 33 | Read transmitter variables | Byte 0 Byte 1 Byte 2 Byte 3 | transm. var. code for slot 0 transm. var. code for slot 1 transm. var. code for slot 2 transm. var. code for slot 3 |  |  | Byte 0 Byte 1 Byte 2-5 Byte 6 Byte 7 Byte 8-11 Byte 12 Byte 13 Byte 14-17 Byte 18 Byte 19 Byte 20-23 | transm. variable code for slot 0 units code for slot 0 variable for slot 0 transm. variable code for slot 1 units code for slot 1 variable for slot 1 transm. variable code for slot 2 units code for slot 2 variable for slot 2 transm. variable code for slot 3 units code for slot 3 variable for slot 3 | (F) (F) (F) (F) |
|  |  | (truncated after last requested code) |  |  |  |  | (truncated after last requested variable) |  |  |  |  |
| 34 | Write damping value | Byte 0-3 | damping value (seconds) | (F) |  | as in command |  |
| 35 | Write range values | Byte 0 Byte 1-4 Byte 5-8 | range units code upper range value lower range value | (F) (F) |  | as in command |  |
| 36 | Set upper range value (= push SPAN button) |  | none |  |  | none |  |
| 37 | Set lower range value (= push ZERO button) |  | none |  |  | none |  |
| 38 | Reset "configuration changed" flag |  | none |  |  | none |  |
| 39 | EEPROM control | Byte 0 | EEPROM control code* |  |  | as in command |  |
|  |  | * 0 = burn EEPROM, 1 = copy EEPROM to RAM. |  |  |  |  |  |  |  |
| 40 | Enter/exit fixed current mode | Byte 0-3 | current (mA)* | (F) |  | as in command |  |
|  |  | * 0 = exit fixed current mode. |  |  |  |  |  |  |  |
| 41 | Perform device self- test |  | none |  |  | none |  |
| 42 | Perform master reset |  | none |  |  | none |  |
| 43 | Set (trim) PV zero |  | none |  |  | none |  |
| 44 | Write PV units | Byte 0 | PV units code |  |  | as in command |  |
| 45 | Trim DAC zero | Byte 0-3 | measured current (mA) | (F) |  | as in command |  |
| 46 | Trim DAC gain | Byte 0-3 | measured current (mA) | (F) |  | as in command |  |
| 47 | Write transfer function | Byte 0 | transfer function code |  |  | as in command |  |
| 48 | Read additional device status |  | none |  | Byte 0-5 Byte 6-7 Byte 8-10 Byte 11-13 Byte 14-24 | device-specific status operational modes (5.1) analogue outputs saturated* (5.1) analogue outputs fixed* (5.1) device-specific status | (B) (B) (B) (B) |
|  |  |  |  |  | * 24 bits each: LSB ... MSB refers to AO #1 ...# 24. (Response is truncated after last byte implemented) |  |  |  |  |

| 49 | Write PV sensor serial number | Byte 0-2 | sensor serial number |  |  | as in command |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 50 | Read dynamic variable assignments (4.1) |  | none |  | Byte 0 Byte 1 Byte 2 Byte 3 | PV transmitter variable code SV transmitter variable code TV transmitter variable code FV transmitter variable code |  |
| 51 | Write dynamic variable assignments (4.1) | Byte 0 Byte 1 Byte 2 Byte 3 | PV transmitter variable code SV transmitter variable code TV transmitter variable code FV transmitter variable code |  |  | as in command |  |
| 52 | Set transmitter variable zero (4.1) | Byte 0 | transmitter variable code |  |  | as in command |  |
| 53 | Write transmitter variable units (4.1) | Byte 0 Byte 1 | transmitter variable code transm. variable units code |  |  | as in command |  |
| 54 | Read transmitter variable information (4.1) | Byte 0 | transmitter variable code |  | Byte 0 Byte 1-3 Byte 4 Byte 5-8 Byte 9-12 Byte 13-16 Byte 17-20 | transmitter variable code transm. var. sensor serial number transm. var. limits units code transm. variable upper limit transm. variable lower limit transm. var. damping value (sec.) transm. var. minimum span (5.0) | (F) (F) (F) (F) |
| 55 | Write transmitter variable damping value (4.1) | Byte 0 Byte 1-4 | transmitter variable code transmitter variable damping value (seconds) | (F) |  | as in command |  |
| 56 | Write transmitter variable sensor serial number (4.1) | Byte 0 Byte 1-3 | transmitter variable code transmitter variable sensor serial number |  |  | as in command |  |
| 57 | Read unit tag, descriptor, date (5.0) |  | none |  | Byte 0-5 Byte 6-17 Byte 18-20 | unit tag (8 characters) unit descriptor (16 characters) unit date | (A) (A) (D) |
| 58 | Write unit tag, descriptor, date (5.0) | Byte 0-5 Byte 6-17 Byte 18-20 | unit tag (8 characters) unit descriptor (16 chars) unit date | (A) (A) (D) |  | as in command |  |
| 59 | Write number of response preambles (5.0) | Byte 0 | number of response preambles |  |  | as in command |  |
| 60 | Read analogue output and percent of range (5.1) | Byte 0 | analogue out. number code |  | Byte 0 Byte 1 Byte 2-5 Byte 6-9 | analogue output number code analogue output units code analogue output level analogue output percent of range | (F) (F) |
| 61 | Read dynamic variables and PV analogue output (5.1) |  | none |  | Byte 0 Byte 1-4 Byte 5 Byte 6-9 Byte 10 Byte 11-14 Byte 15 Byte 16-19 Byte 20 Byte 21-24 | PV analogue output units code PV analogue output level PV units code Primary variable SV units code Secondary variable TV units code Third variable FV units code Fourth variable | (F) (F) (F) (F) (F) |
|  |  |  |  |  | ( truncated after last supported variable) |  |  |  |  |

| 62 | Read analogue outputs (5.1) | Byte 0 Byte 1 Byte 2 Byte 3 | analogue output number code for slot 0 analogue output number code for slot 1 analogue output number code for slot 2 analogue output number code for slot 3 |  | Byte 0 Byte 1 Byte 2-5 Byte 6 Byte 7 Byte 8-11 Byte 12 Byte 13 Byte 14-17 Byte 18 Byte 19 Byte 20-23 | slot 0 analogue output number code slot 0 units code slot 0 level slot 1 analogue output number code slot 1 units code slot 1 level slot 2 analogue output number code slot 2 units code slot 2 level slot 3 analogue output number code slot 3 units code slot 3 level | (F) (F) (F) (F) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | (truncated after last requested code) |  |  |  |  | (truncated after last requested level) |  |  |  |  |
| 63 | Read analogue output information (5.1) | Byte 0 | analogue output number code |  | Byte 0 Byte 1 Byte 2 Byte 3 Byte 4-7 Byte 8-11 Byte 12-15 | analogue output number code analogue output alarm select code analogue out. transfer function code analogue output range units code analogue output upper range value analogue output lower range value analogue output additional damping value (sec) | (F) (F) (F) |
| 64 | Write analogue output additional damping value (5.1) | Byte 0 Byte 1-4 | analogue out. number code analogue output additional damping value (sec) | (F) |  | as in command |  |
| 65 | Write analogue output range values (5.1) | Byte 0 Byte 1 Byte 2-5 Byte 6-9 | analogue out. number code an. out. range units code an. out. upper range value an. out. lower range value | (F) (F) |  | as in command |  |
| 66 | Enter/exit fixed analogue output mode (5.1) | Byte 0 Byte 1 Byte 2-5 | analogue out. number code analogue output units code analogue output level* | (F) |  | as in command |  |
|  |  | * "not a number" exits fixed output mode |  |  |  |  |  |  |  |
| 67 | Trim analogue output zero (5.1) | Byte 0 Byte 1 Byte 2-5 | analogue out. number code analogue out. units code externally-measured analogue output level | (F) |  | as in command |  |
| 68 | Trim analogue output gain (5.1) | Byte 0 Byte 1 Byte 2-5 | analogue out. number code analogue out. units code externally-measured analogue output level | (F) |  | as in command |  |
| 69 | Write analogue output transfer function (5.1) | Byte 0 Byte 1 | analogue out. number code an. out. transfer funct. code |  |  | as in command |  |
| 70 | Read analogue output endpoint values (5.1) | Byte 0 | analogue out. number code |  | Byte 0 Byte 1 Byte 2-5 Byte 6-9 | analogue output number code analogue out. endpoint units code analogue out. upper endpoint value analogue out. lower endpoint value | (F) (F) |
| 107 | Write burst mode transmitter variables (for Command #33) (5.1) | Byte 0 Byte 1 Byte 2 Byte 3 | transm. var. code for slot 0 transm. var. code for slot 1 transm. var. code for slot 2 transm. var. code for slot 3 |  |  | as in command |  |
| 108 | Write burst mode command number (5.0) | Byte 0 | burst mode command number |  |  | as in command |  |

| 109 | Burst mode control (5.0) | Byte 0 | burst mode control code (0 = exit, 1 = enter) |  |  | as in command |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 110 | Read all dynamic variables (5.0) |  | none |  | Byte 0 Byte 1-4 Byte 5 Byte 6-9 Byte 10 Byte 11-14 Byte 15 Byte 16-19 | PV units code PV value SV units code SV value TV units code TV value FV units code FV value | (F) (F) (F) (F) |