- HCF_LIT-20 Rev. 3.0:  Errata 2		10 June 2008

- Table A3.3. Command response codes with multiple meanings

Code 29, “Invalid span”, is also supported by Command #35.  The relevant line should be:

| Code | Warning (W) or Error (E) | Commands | Alternative meanings |
| --- | --- | --- | --- |
| 29 | E | 35, 36, 37 | Invalid span |

- Table 9.4.  Field device status

- and Table A3.4.  Field device status

The descriptions for bits 0 and 1 were interchanged.  The tables should be as follows:

| Bit | Status indication | Meaning |
| --- | --- | --- |
| Bit 7 | Field device malfunction | Measurements should not be trusted |
| Bit 6 | Configuration changed 1 | Set whenever a configuration change is made by any host, or through a local operator interface. A master should recognise this bit as a warning to re-read any cached configuration information, and should then clear the bit by sending Command #38 |
| Bit 5 | Cold start 1 | Set, for one transaction only to each master, when a field device is powered up |
| Bit 4 | More status available | Use Command #48 to retrieve further information (see section 9.5) |
| Bit 3 | Analogue output fixed | The device is in multidrop mode, or the output has been set at a fixed value for testing. This bit applies only to Analogue Output #1 3 |
| Bit 2 | Analogue output saturated | The measurement (for Analogue Output #1) is out of range, or the actuator input current is out of range 2, 3 |
| Bit 1 | Non-primary variable out of limits | As below, but for one or more other variables. There is no way to identify the specific variable (unless Command #48 gives further information) |
| Bit 0 | Primary variable out of limits | The primary measurement is outside the sensor operating limits. So, not only is the analogue signal unreliable, but so is the digital value read by HART commands |